## Sheet1
FGS MASTER OVERRIDE REGISTER - CCR
no | Time in | Module Parameter | Description | Alarm | Message | Priority | Status | Date on | Requested by | Date off | Removal Requested by
1 | 2026-01-29 09:12 | 77ATFZP01-301 | P01 flare vent header GAS detector bypass (forced in logic) | FGS bypass |  | critical | second event - risk assessment ongoing | 2026-01-29 | OIM
2 | 2026-01-29 09:12 | 77ATFZP01-302 | P01 flare vent header GAS detector bypass (forced in logic) | FGS bypass |  | critical | second event - risk assessment ongoing | 2026-01-29 | OIM
3 | 2025-12-25 11:07 | 25GAHFZGTC1-301 | P04 MRC1 enclosure Gas detector bypass | SIS bypass |  | critical | risk assessment with vendor ongoing | 2025-12-25 | Startup Manager
4 | 2025-12-25 12:38 | 25BAHFZGTC1-301 | P04 MRC1 enclosure Fire detector bypass | SIS bypass |  | critical | risk assessment with vendor ongoing | 2025-12-25 | Startup Manager
5 | 2025-12-25 12:38 | 25XSY-9003 | P04 MRC1 water mist release confirmed from package | SIS bypass |  | critical | risk assessment with vendor ongoing | 2025-12-25 | Startup Manager
6 | 2026-01-06 04:30 | 77ATFZS02-GD02 | S02 Gas detectort | FGS bypass | MOS active |  | Bleed system 23 filter | 2026-01-06 | Jacky Zhang
7 | 2025-12-17 17:11 | 70XA_7001 | Snuffing system LCP fault alarm at FZP01 | FGS bypass | MOS active |  | LCP fault | 2025-12-17 | Startup Manager
8 | 2025-12-14 06:46 | 95XA_8010 | Laboratory loss of ventilation alarm | FGS bypass | MOS active |  | bypass required - need HVAC | 2025-12-17 | Startup Manager
9 | 2025-12-13 11:49 | 77BFFZS02_403 | Flame detector S02 Deck 4 | FGS bypass | MOS active |  | MOS required - waiting for replacement parts | 2025-12-13 | Startup Manager
10 | 2025-12-01 13:25 | 77BEFZEDG_006 | U Deck Em.Ele Room HSSD Alarm | FGS bypass | MOS active |  | need bypass - too much sensitivity | 2025-12-01 | Startup Manager
11 | 2025-12-01 13:25 | 77BEFZABAD_002 | Instrument Equipment Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
12 | 2025-12-01 13:25 | 77BEFZABUD_003 | Telecom Auxiliary Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
13 | 2025-12-01 13:25 | 77BEFZABED_005 | Hull UPS Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
14 | 2025-12-01 13:25 | 77BEFZABDD_004 | Telecom Equipment Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
15 | 2025-11-18 13:25 | 77TLDFZS04_208 | S04 Topside Deck 4 | FGS bypass | MOS active |  | MOS required - waiting for replacement parts | 2025-11-18 | Startup Manager |  | punch + LTI required
16 | 2025-11-18 13:25 | 77PDT_1241 | Engine Driven FWP container overpressure alarms | FGS bypass | MOS active |  | MOS required - waiting for replacement parts | 2025-11-18 | Startup Manager
17 | 2025-09-22 07:00 | 77ZS_1501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
18 | 2025-09-22 07:00 | 77ZS_1502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
19 | 2025-09-22 07:00 | 77ZS_2501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
20 | 2025-09-22 07:00 | 77ZS_2502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
21 | 2025-09-22 07:00 | 77ZS_3501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
22 | 2025-09-22 07:00 | 77ZS_3502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
23 | 2025-09-22 07:00 | 77ZS_4501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
24 | 2025-09-22 07:00 | 77ZS_4502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
25 | 2025-09-22 07:00 | 77ZS_5501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
26 | 2025-09-22 07:00 | 77LIT_3502 | Foam Tank level indication | FGS bypass | MOS active |  | MOS required, level is too low | 2025-09-22 | Startup Manager
27 | 2025-09-22 07:00 | 70LKFZEHSE_244 | Inergen System Leakage alarm | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-22 | Startup Manager
28 | 2025-09-22 07:00 | 70CFFZEHSE_223 | Inergen LCP fault alarm | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-22 | Startup Manager
29 | 2025-09-22 07:00 | 95PDIT_0203 | E501 DP of 95-FAN-111 | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-22 | Startup Manager
30 | 2025-12-19 17:11 | FD-BYPASS | FALME DETECTORS OVERALL BYPASS TOPSIDE/OPEN areas | FGS bypass | MOS active |  | waiting for Flame Detectors replacement new model | 2025-12-19 17:11 | Startup Manager
31 | 2025-09-11 07:00 | 77ZS_315 | Air Lock FZ-FSW | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
32 | 2025-09-11 07:00 | 77ZS_319 | Air Lock PS | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
33 | 2025-09-11 07:00 | 77ZS_316 | Air Lock | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
34 | 2025-09-11 07:00 | 77ZS_317 | Air Lock | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
35 | 2025-09-11 07:00 | 77ZS_321 | Air Lock FZPRSW | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
36 | 2025-09-11 07:00 | 77ZS_320 | Air Lock FZPRSW | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
37 | 2025-09-11 07:00 | 77ZS_314 | Air Lock | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
38 | 2025-09-11 07:00 | 77ZS_318 | Air Lock SB | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
39 | 2025-09-11 07:00 | 70XZ_0331 | Inergen AFT HULL Abort indication | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-11 07:00 | Startup Manager
40 | 2025-09-11 07:00 | 70XA_0337 | Inergen AFT HULL Common Alarm | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-11 07:00 | Startup Manager
41 | 2026-01-23 | 77ATFZFGCM-GD03 | Gas Voting Feed Gas Custody Metering area | FGS bypass | MOS active |  | false alarms - need to be calibrated | 2026-01-23 | Zhang
42 | 2025-12-17 | 77ZS_308 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
43 | 2025-12-17 | 77ZS_309 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
44 | 2025-12-17 | 77ZS_312 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
45 | 2025-12-17 | 77ZS_313 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
46 | 2025-12-17 | 77ZS_310 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
47 | 2025-12-17 | 77ZS_311 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
48 | 2025-12-17 | 77ZS_306 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
49 | 2025-12-17 | 77ZS_303 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
50 | 2025-12-17 | 77ZS_307 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
51 | 2025-12-17 | 77ZS_301 | Air Lock | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
52 | 2025-12-17 | 77ZS_302 | Air Lock | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
53 | 2026-01-27 | 77ATFZABED_GD07 | H2 in UPS LQ-E deck room | FGS bypass | MOS active |  | H2 spikes randomly | 2026-01-27 | Liu Wenlong |  | Risk assessment and add 10s filter delay/MOC
54 | 2026-01-28 | 77BHFZCRA4-D918 | Main Deck crane 4 Machinery room flame FACP | FACP bypass | MOS active |  | in alarm when Crane run and temp ony 40C | 2026-01-28 | Liu Wenlong
55 | 2026-01-28 | 77BHFZCRA2-D915 | Main Deck crane 2 Machinery room flame FACP | FACP bypass | MOS active |  | in alarm when Crane run and temp ony 40C | 2026-01-28 | Liu Wenlong
56 | 2026-01-28 | 77BHFZEDFC-H903 | FWD Fire Water Pump Container heat detector | FACP bypass | MOS active |  | Framo FWP alarm when op temp > 40C | 2026-01-28 | Liu Wenlong
57 | 2026-01-28 | 77BHFZEDFC-H904 | FWD Fire Water Pump Container heat detector | FACP bypass | MOS active |  | Framo FWP alarm when op temp > 40C | 2026-01-28 | Liu Wenlong
58 | 2026-01-28 | 77BHFZEDFC-H905 | FWD Fire Water Pump Container heat detector | FACP bypass | MOS active |  | Framo FWP alarm when op temp > 40C | 2026-01-28 | Liu Wenlong
59 | 2026-01-28 | 77BSFZESDG-G044 | Generateor Room SB smoke detector | FACP bypass | MOS active |  |  | 2026-01-28 | Liu Wenlong
60 | 2026-01-28 | 77BSFZFHER_H502 | Forward Engine room 4th deck heat detector | FACP bypass | MOS active |  |  | 2026-01-28 | Liu Wenlong
61 | 2026-01-28 | 77BSFZABMD-F011 | Temporary smoking area M deck | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
62 | 2026-01-28 | 77BSFZABMD-F012 | Temporary smoking area M deck | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
63 | 2026-01-28 | 77BSFZEHSE-K508 | E-House detector fault | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
64 | 2026-01-28 | 77BSFZVSPS-V028 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
65 | 2026-01-28 | 77BSFZVSPS-V016 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
66 | 2026-01-28 | 77BSFZVSPS-V940 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
67 | 2026-01-28 | 77BSFZVSPS-V942 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
68 | 2026-01-29 | 77BAH-202 | Confirmed single MCP fire alarm | FGS bypass | MOS active |  | to avoid wrong logic to activate ESD2 | 2026-01-29 | OIM |  | wait for download to clear