## Overrides
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
FGS MASTER OVERRIDE REGISTER - CCR
No | Approved | Closed | Time In | Module Parameter | Description | Alarm | Message | Priority | Status | Date On | Requested By | Date Off | Removal Requested By
1 |  |  | 2025-09-08 | 24TSLL-0504 | 24-T-001 deethanizer liq.outlet temp LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-09-08 | Startup Manager
2 |  |  | 2025-09-08 | 34XL-7001C | 34-C-001C LNG BOG compr.Running status from UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-09-08 | Startup Manager
3 |  |  | 2025-09-08 | 34PSHL-0412 | 34-C-001C LNG BOG compr.HP section discharge pressure | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-09-08 | Startup Manager
4 |  |  | 2025-09-08 | 34XSLL-7001B | 34-C-001C LNG BOG Depressurized trip notification from UCP | SIS bypass | MOS active |  | Re-instate and close BDV | 2025-09-08 | Startup Manager
5 |  |  | 2025-09-08 | 34XSLL-7001A | 34-C-001C LNG BOG Pressurized trip notification from UCP | SIS bypass | MOS active |  | Re-instate and close BDV | 2025-09-08 | Startup Manager
6 |  |  | 2025-09-08 | 34XSLL-8001B | 34-C-001B LNG BOG Depressurized trip notification from UCP | SIS bypass | MOS active |  | Re-instate and close BDV | 2025-09-08 | Startup Manager
7 |  |  | 2025-09-08 | 34PDSLL-0313 | 34-C-001B LNG BOG primary seal gas Ni sys protection | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-09-08 | Startup Manager
8 |  |  | 2025-09-08 | 24PSLL-0521 | 24-T-001 deethanizer pressure LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-09-08 | Startup Manager
9 |  |  | 2025-09-08 | 24TSLL-0311 | 24PKG-004_E-002 Deethanizer reflux pass A out temp.LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-09-08 | Startup Manager
10 |  |  | 2025-09-09 | 25XSLL-9001A | Pressurized trip from MKVIes MRC1 UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
11 |  |  | 2025-09-09 | 25XSLL-9001B | Depressurized trip from MKVIes MRC1 UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
12 |  |  | 2025-09-11 07:00 | 77ZS_315 | Air Lock FZ-FSW | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
13 |  |  | 2025-09-11 07:00 | 77ZS_319 | Air Lock PS | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
14 |  |  | 2025-09-11 07:00 | 77ZS_316 | Air Lock | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
15 |  |  | 2025-09-11 07:00 | 77ZS_317 | Air Lock | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
16 |  |  | 2025-09-11 07:00 | 77ZS_321 | Air Lock FZPRSW | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
17 |  |  | 2025-09-11 07:00 | 77ZS_320 | Air Lock FZPRSW | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
18 |  |  | 2025-09-11 07:00 | 77ZS_314 | Air Lock | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
19 |  |  | 2025-09-11 07:00 | 77ZS_318 | Air Lock SB | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-11 07:00 | Startup Manager
20 |  |  | 2025-09-11 07:00 | 70XZ_0331 | Inergen AFT HULL Abort indication | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-11 07:00 | Startup Manager
21 |  |  | 2025-09-11 07:00 | 70XA_0337 | Inergen AFT HULL Common Alarm | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-11 07:00 | Startup Manager
22 |  |  | 2025-09-20 | 34XSLL-9001B | 34-C-001A Depressurized trip notification from MKVIes UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
23 |  |  | 2025-09-20 | 24XSLL-9004A | 34-C-001A Pressurized trip notification from MKVIes UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
24 |  |  | 2025-09-22 07:00 | 77ZS_1501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
25 |  |  | 2025-09-22 07:00 | 77ZS_1502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
26 |  |  | 2025-09-22 07:00 | 77ZS_2501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
27 |  |  | 2025-09-22 07:00 | 77ZS_2502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
28 |  |  | 2025-09-22 07:00 | 77ZS_3501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
29 |  |  | 2025-09-22 07:00 | 77ZS_3502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
30 |  |  | 2025-09-22 07:00 | 77ZS_4501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
31 |  |  | 2025-09-22 07:00 | 77ZS_4502 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
32 |  |  | 2025-09-22 07:00 | 77ZS_5501 | Airlock Door open limit switch alarm | FGS bypass | MOS active |  | MOS required, requested by OIM | 2025-09-22 | Startup Manager
33 |  |  | 2025-09-22 07:00 | 77LIT_3502 | Foam Tank level indication | FGS bypass | MOS active |  | MOS required, level is too low | 2025-09-22 | Startup Manager
34 |  |  | 2025-09-22 07:00 | 70LKFZEHSE_244 | Inergen System Leakage alarm | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-22 | Startup Manager
35 |  |  | 2025-09-22 07:00 | 70CFFZEHSE_223 | Inergen LCP fault alarm | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-22 | Startup Manager
36 |  |  | 2025-09-22 07:00 | 95PDIT_0203 | E501 DP of 95-FAN-111 | FGS bypass | MOS active |  | need bypass, not working - see punches | 2025-09-22 | Startup Manager
37 |  |  | 2025-10-12 | 24PSLL-0413 | 24-PKG-001_C-001 Treated Gas Comp inlet pressure LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
38 |  |  | 2025-10-12 | 24PSHL-0430 | 24-PKG-001_C-001 Treated Gas Comp outlet pressure HH | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
39 |  |  | 2025-10-16 | 29LSLL-0108 | 29-V-002 LNG Buffer Dum Level LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
40 |  |  | 2025-10-16 | 34PSLL-0210 | 34-C-001A LNG BOG comp.HP.Section press LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
41 |  |  | 2025-10-16 | 34PSLL-0209 | 34-C-001A LNG BOG comp.LP.Section press LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
42 |  |  | 2025-10-16 | 34PDSLL-0213 | 34-C-001A LNG BOG compr.Primary seal gas Ni.sys.protect | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
43 |  |  | 2025-10-16 | 34PSHL-0212 | 34-C-001A LNG BOG comp.HP.Section pressure | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
44 |  |  | 2025-10-16 | 24PSHL-0901 | 24-PKG-002_C-002 Feed Gas Booster compr. Outlet press. | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-16 | Startup Manager
45 |  |  | 2025-10-20 | 25FSLL-0206 | HP MR liquid from 25-V-002 Flow LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-20 | Startup Manager
46 |  |  | 2025-10-20 | 34XA-5002 | 34-C-002B LPG BOG comp. Em.Stop Active from Vendor UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-20 | Startup Manager
47 |  |  | 2025-10-20 | 34XL-5002 | 34-C-002B LPG BOG comp.Running Status from Vendor UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-20 | Startup Manager
48 |  |  | 2025-10-20 | 34XL-6002 | 34-C-002A LPG BOG comp.Running Status from Vendor UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-20 | Startup Manager
49 |  |  | 2025-10-20 | 34XA-6002 | 34-C-002A LPG BOG comp. Em.Stop Active from Vendor UCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-20 | Startup Manager
50 |  |  | 2025-10-22 | 86XL-0027 | ESL connect to condensate Tank indication | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-10-22 | Startup Manager
51 |  |  | 2025-11-10 | 24XSLL-8001A | 24-PKG-001 Pressurized trip from MarkVIeS UCP | SIS bypass | MOS active |  | keep inhibited | 2025-11-10 | Startup Manager
52 |  |  | 2025-11-10 | 24XSLL-8001B | 24-PKG-001 Depressurized trip from MarkVIeS UCP | SIS bypass | MOS active |  | Reinstate close BDV | 2025-11-10 | Startup Manager
53 |  |  | 2025-11-13 | 25TSLL-1507 | MR Desuperheater discharge temperature LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-11-13 | Startup Manager
54 |  |  | 2025-11-18 13:25 | 77TLDFZS04_208 | S04 Topside Deck 4 | FGS bypass | MOS active |  | MOS required - waiting for replacement parts | 2025-11-18 | Startup Manager
55 |  |  | 2025-11-18 13:25 | 77PDT_1241 | Engine Driven FWP container overpressure alarms | FGS bypass | MOS active |  | MOS required - waiting for replacement parts | 2025-11-18 | Startup Manager
56 |  |  | 2025-11-26 | 35FSLL-0105 | Off-spec LPG from 32-P-003 Flow LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-11-26 | Startup Manager
57 |  |  | 2025-12-01 13:25 | 77BEFZEDG_006 | U Deck Em.Ele Room HSSD Alarm | FGS bypass | MOS active |  | need bypass - too much sensitivity | 2025-12-01 | Startup Manager
58 |  |  | 2025-12-01 13:25 | 77BEFZABAD_002 | Instrument Equipment Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
59 |  |  | 2025-12-01 13:25 | 77BEFZABUD_003 | Telecom Auxiliary Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
60 |  |  | 2025-12-01 13:25 | 77BEFZABED_005 | Hull UPS Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
61 |  |  | 2025-12-01 13:25 | 77BEFZABDD_004 | Telecom Equipment Room HSSD Alarm | FGS bypass | MOS active |  | bypass required due to exhaust from flotel | 2025-12-01 | Startup Manager
62 |  |  | 2025-12-03 | 32XA-0911 | LSD2 Trip from LPG offloading hose 32-PKG-020 RCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-03 | Startup Manager
63 |  |  | 2025-12-03 | 32XA-0912 | LSD1 Trip from LPG offloading hose 32-PKG-020 RCP | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-03 | Startup Manager
64 |  |  | 2025-12-06 | 76HS-1342 | Process Deck ESD-2 PB | SIS bypass | MOS active |  | re-instate | 2025-12-06 | Startup Manager
65 |  |  | 2025-12-07 | 26FSLL-0206 | HP MR liquid from 26-V-002 Flow LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-07 | Startup Manager
66 |  |  | 2025-12-07 | 26TSHH-0311 | High Temp LNG to rundown tank BAHX pass A out | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-07 | Startup Manager
67 |  |  | 2025-12-08 | 30PSHH-1304 | warming gas header to LNG cargo tanks | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-08 | Startup Manager
68 |  |  | 2025-12-10 | 25PSLL-1227 | 25-C-001 MRC 1st stage suction pressure LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-10 | Startup Manager
69 |  |  | 2025-12-10 | 25TSHH-0311 | LNG Rundown from 25-E-001 Pass A temp.HH | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-10 | Startup Manager
70 |  |  | 2025-12-10 | 25PSLL-4028 | 25-C-001 MRC2nd stage suction pressure LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-10 | Startup Manager
71 |  |  | 2025-12-10 | 35FSLL-0314 | 35-P-001A/B cond.stabilizer reflux pump flow LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-10 | Startup Manager
72 |  |  | 2025-12-12 | 26TSLL-1507 | MR Desuperheater discharge temperature LL | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-12 | Startup Manager
73 |  |  | 2025-12-13 | 25ESDZTO-1715 | 25V-003 MRC disc,spt. HP out 33V-001 | SIS bypass | MOS active |  | Inhibit (Warm End Startup only) | 2025-12-13 | Startup Manager
74 |  |  | 2025-12-13 11:49 | 77BFFZS02_403 | Flame detector S02 Deck 4 | FGS bypass | MOS active |  | MOS required - waiting for replacement parts | 2025-12-13 | Startup Manager
75 |  |  | 2025-12-14 06:46 | 95XA_8010 | Laboratory loss of ventilation alarm | FGS bypass | MOS active |  | bypass required - need HVAC | 2025-12-17 | Startup Manager
76 |  |  | 2025-12-17 | 77ZS_308 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
77 |  |  | 2025-12-17 | 77ZS_309 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
78 |  |  | 2025-12-17 | 77ZS_312 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
79 |  |  | 2025-12-17 | 77ZS_313 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
80 |  |  | 2025-12-17 | 77ZS_310 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
81 |  |  | 2025-12-17 | 77ZS_311 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
82 |  |  | 2025-12-17 | 77ZS_306 | Air Lock SB | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
83 |  |  | 2025-12-17 | 77ZS_303 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
84 |  |  | 2025-12-17 | 77ZS_307 | Air Lock PS | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
85 |  |  | 2025-12-17 | 77ZS_301 | Air Lock | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
86 |  |  | 2025-12-17 | 77ZS_302 | Air Lock | FGS bypass | MOS active |  | No gas in the plant | 2025-12-17 | Liu Wenlong
87 |  |  | 2025-12-17 17:11 | 70XA_7001 | Snuffing system LCP fault alarm at FZP01 | FGS bypass | MOS active |  | LCP fault | 2025-12-17 | Startup Manager
88 |  |  | 2025-12-19 17:11 | FD-BYPASS | FALME DETECTORS OVERALL BYPASS TOPSIDE/OPEN areas | FGS bypass | MOS active |  | waiting for Flame Detectors replacement new model | 2025-12-19 17:11 | Startup Manager
89 |  |  | 2025-12-25 11:07 | 25GAHFZGTC1-301 | P04 MRC1 enclosure Gas detector bypass | SIS bypass |  | critical | risk assessment with vendor ongoing | 2025-12-25 | Startup Manager
90 |  |  | 2025-12-25 12:38 | 25BAHFZGTC1-301 | P04 MRC1 enclosure Fire detector bypass | SIS bypass |  | critical | risk assessment with vendor ongoing | 2025-12-25 | Startup Manager
91 |  |  | 2025-12-25 12:38 | 25XSY-9003 | P04 MRC1 water mist release confirmed from package | SIS bypass |  | critical | risk assessment with vendor ongoing | 2025-12-25 | Startup Manager
92 |  |  | 2025-12-26 | 30S-1000 | USD 30-CTK-001 SD | SIS bypass | MOS active |  | Low pressure | 2025-12-26 | Osumarin
93 |  |  | 2025-12-26 | 30S-2000 | USD 30-CTK-002 SD | SIS bypass | MOS active |  | Low pressure | 2025-12-26 | Osumarin
94 |  |  | 2025-12-29 | 26XV-1356 | 26-V-002 stage 2 suction isol. Valve bypass | SIS bypass | Valve Open |  |  | 2025-12-29
95 |  |  | 2025-12-31 | 32S-1003 | LSD trip LPG Cargo pump A 32P-001A | SIS bypass | MOS active |  |  | 2025-12-31 | Yaphy
96 |  |  | 2025-12-31 | 32S-1004 | LSD trip LPG Cargo pump A 32P-001B | SIS bypass | MOS active |  |  | 2025-12-31 | Yaphy
97 |  |  | 2025-12-31 | 32S-2003 | LSD trip LPG Cargo pump A 32P-002A | SIS bypass | MOS active |  |  | 2025-12-31 | Yaphy
98 |  |  | 2025-12-31 | 32S-2004 | LSD trip LPG Cargo pump A 32P-002B | SIS bypass | MOS active |  |  | 2025-12-31 | Yaphy
99 |  |  | 2026-01-04 | 22TSHH-0409 | 22-E-003A/B amine exchanger lean amine temp HH | SIS bypass | MOS active |  | startup bypass | 2026-01-04
100 |  |  | 2026-01-04 | 45LSHH-0307B | 45-V-002 LP fuel gas surge drum level HH | SIS bypass | MOS active |  | need tstartup tea to remove | 2026-01-04
101 |  |  | 2026-01-04 | 30LSVH-0102 | GO LNG Cargo tank 30-CTK-001 level | SIS bypass | MOS active |  | need tstartup tea to remove | 2026-01-04
102 |  |  | 2026-01-04 | 36PSHL-0204 | Condensate cargo pump 36P-002 outlet pressure | SIS bypass | MOS active |  | need tstartup tea to remove | 2026-01-04
103 |  |  | 2026-01-06 04:30 | 77ATFZS02-GD02 | S02 Gas detectort | FGS bypass | MOS active |  | Bleed system 23 filter | 2026-01-06 | Jacky Zhang
104 |  |  | 2026-01-10 | 36YYT-0001 | trip condensate pumps | SIS bypass | MOS active |  | condensate pump test | 2026-01-10 | Li Jian
105 |  |  | 2026-01-10 | 36YYT-0002 | trip condensate pumps | SIS bypass | MOS active |  | condensate pump test | 2026-01-10 | Li Jian
106 |  |  | 2026-01-10 | 36YYT-0003A | trip condensate pumps | SIS bypass | MOS active |  | condensate pump test | 2026-01-10 | Li Jian
107 |  |  | 2026-01-10 | 36YYT-0003B | trip condensate pumps | SIS bypass | MOS active |  | condensate pump test | 2026-01-10 | Li Jian
108 |  |  | 2026-01-10 | 35LSHH-0313ABC | 35-V-001 condensate stabilizer reflux drum L | SIS bypass | 35S-0007 force normal |  | forced in logic! | 2026-01-10 | kalid
109 |  |  | 2026-01-20 | 22LSHH-0104ABC | 22-T-001 level for oil skimming | SIS bypass | 22S-0021 |  |  | 2026-01-20 | Zhang Shengyun
110 |  |  | 2026-01-20 | 22LSHH-0304ABC | 22-V-001 lvel for oil skimming | SIS bypass | 22S-0025 |  |  | 2026-01-20 | Zhang Shengyun
111 |  |  | 2026-01-23 | 77ATFZFGCM-GD03 | Gas Voting Feed Gas Custody Metering area | FGS bypass | MOS active |  | false alarms - need to be calibrated | 2026-01-23 | Zhang
112 |  |  | 2026-01-24 | 26FSHH-0120 | NG to 26 cold box flow rate HH | SIS bypass | MOS active |  |  | 2026-01-24 | Zhang Shengyun
113 |  |  | 2026-01-24 | 26FSLL-0120 | NG to 26 cold box flow rate LL | SIS bypass | MOS active |  |  | 2026-01-24 | Jocky Zhang
114 |  |  | 2026-01-27 | 77ATFZABED_GD07 | H2 in UPS LQ-E deck room | FGS bypass | MOS active |  | H2 spikes randomly | 2026-01-27 | Liu Wenlong
115 |  |  | 2026-01-27 | 26TSHH9406B | Enclosure FT disabeld of MRC2 | BH EWS | override |  | fault alarms | 2026-01-27 | Rugolo Gianluca
116 |  |  | 2026-01-28 | 77BHFZCRA4-D918 | Main Deck crane 4 Machinery room flame FACP | FACP bypass | MOS active |  | in alarm when Crane run and temp ony 40C | 2026-01-28 | Liu Wenlong
117 |  |  | 2026-01-28 | 77BHFZCRA2-D915 | Main Deck crane 2 Machinery room flame FACP | FACP bypass | MOS active |  | in alarm when Crane run and temp ony 40C | 2026-01-28 | Liu Wenlong
118 |  |  | 2026-01-28 | 77BHFZEDFC-H903 | FWD Fire Water Pump Container heat detector | FACP bypass | MOS active |  | Framo FWP alarm when op temp > 40C | 2026-01-28 | Liu Wenlong
119 |  |  | 2026-01-28 | 77BHFZEDFC-H904 | FWD Fire Water Pump Container heat detector | FACP bypass | MOS active |  | Framo FWP alarm when op temp > 40C | 2026-01-28 | Liu Wenlong
120 |  |  | 2026-01-28 | 77BHFZEDFC-H905 | FWD Fire Water Pump Container heat detector | FACP bypass | MOS active |  | Framo FWP alarm when op temp > 40C | 2026-01-28 | Liu Wenlong
121 |  |  | 2026-01-28 | 77BSFZESDG-G044 | Generateor Room SB smoke detector | FACP bypass | MOS active |  |  | 2026-01-28 | Liu Wenlong
122 |  |  | 2026-01-28 | 77BSFZFHER_H502 | Forward Engine room 4th deck heat detector | FACP bypass | MOS active |  |  | 2026-01-28 | Liu Wenlong
123 |  |  | 2026-01-28 | 77BSFZABMD-F011 | Temporary smoking area M deck | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
124 |  |  | 2026-01-28 | 77BSFZABMD-F012 | Temporary smoking area M deck | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
125 |  |  | 2026-01-28 | 77BSFZEHSE-K508 | E-House detector fault | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
126 |  |  | 2026-01-28 | 77BSFZVSPS-V028 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
127 |  |  | 2026-01-28 | 77BSFZVSPS-V016 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
128 |  |  | 2026-01-28 | 77BSFZVSPS-V940 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
129 |  |  | 2026-01-28 | 77BSFZVSPS-V942 | Detectors dirty alarms | FACP bypass | MOS active |  |  | 2026-01-28 | OIM
130 |  |  | 2026-01-29 | 22LIT-0503ABC | 22S-0023 and 22S-0027 | SIS bypass | MOS active |  |  | 2026-01-29 | Liu Zianling
131 |  |  | 2026-01-29 | 77BAH-202 | Confirmed single MCP fire alarm | FGS bypass | MOS active |  | to avoid wrong logic to activate ESD2 | 2026-01-29 | OIM
132 |  |  | 2026-01-29 09:12 | 77ATFZP01-301 | P01 flare vent header GAS detector bypass (forced in logic) | FGS bypass |  | critical | second event - risk assessment ongoing | 2026-01-29 | OIM
133 |  |  | 2026-01-29 09:12 | 77ATFZP01-302 | P01 flare vent header GAS detector bypass (forced in logic) | FGS bypass |  | critical | second event - risk assessment ongoing | 2026-01-29 | OIM
134 |  |  | 2026-02-01 14:02 | 77ALL | test from fabio with user | FGS bypass | MOS active | critical | keep it there please | 02/01/26 | Fabio Matricardi
135 |  |  | 1/29/26 9:12 | 77ATFZP01-301 | P01 flare vent header GAS detector bypass (forced in logic) | FGS bypass |  | critical | second event - risk assessment ongoing | 1/29/26 | OIM
136 |  |  | 1/29/26 9:12 | 77ATFZP01-302 | P01 flare vent header GAS detector bypass (forced in logic) | FGS bypass |  | critical | second event - risk assessment ongoing | 1/29/26 | OIM